IO ALLOCATION FUNDAMENTALS

Project Guidelines for VIT Students

DeltaV CHARMs-based signal allocation: from field cable to controller

What this guide will help you do Read an IO Allocation row, understand the physical and software signal path, apply project naming conventions, select the correct CHARM and terminal block, allocate field and spare capacity, and perform a disciplined quality check before issue.

Training basis: the original Sample IO Allocation workbook and the project-specific design rules supplied for this VIT exercise.

Important: naming rules, spare percentages, segregation philosophy and reserved baseplates are project/customer specific. Always confirm the approved project standards before applying this guide to another job.

# Contents

# What IO Allocation means

IO Allocation is the engineering activity that gives every plant signal a complete, traceable home. It links the process tag and cable pair to a physical terminal, a CHARM channel, a baseplate and CIOC/CSLS, then links that CIOC/CSLS to the correct DeltaV controller.

A good allocation is not only a list of addresses. It must satisfy wiring, hardware, software, segregation, spare-capacity, maintainability and future-expansion requirements at the same time.

The central idea Every row should allow another engineer to answer five questions without guessing: What is the signal? Which cable pair carries it? Where is it physically terminated? Which controller owns it? Is the position an actual signal, a wired spare or an unused spare slot?

## End-to-end signal flow

| Step | Physical / software element | What the allocation records |
| --- | --- | --- |
| 1 | Field device | Tag and signal originate in plant |
| 2 | Field cable | Multicore cable number and size |
| 3 | Cable pair | One pair assigned to one signal |
| 4 | CHARM TB | Conductors land on terminal block |
| 5 | CHARM | Signal-specific electronic module |
| 6 | Baseplate / CIOC | Channel is physically located |
| 7 | DeltaV controller | Software assignment completes ownership |

The physical path ends at the CIOC/CSLS hardware, but the engineering path is complete only after the CIOC/CSLS and its channels are assigned to the intended controller in DeltaV software. The System Cabinet and Controller columns record the control ownership; the Marshalling Cabinet, CIOC/CSLS, Baseplate, Channel_No and CHARM_No columns record the physical IO location.

## Cabinet and hardware hierarchy

| SYSTEM CABINET Controller hardware Example: P30-DCS-32001-02 | > | MARSHALLING CABINET 4 CIOCs / CSLS 8 baseplates per CIOC 12 channels per baseplate CHARMs and terminal blocks | > | FIELD Instruments and final elements Multicore cables and pairs |
| --- | --- | --- | --- | --- |

System cabinet: contains the controller hardware. Marshalling cabinet: contains the CIOC/CSLS hardware, baseplates, CHARMs and terminal blocks. DeltaV software: associates the CIOC/CSLS and its channels with the controller.

# How to read one allocation row

Read from the field side toward the controller side. The following example is an actual pattern from the workbook.

| Stage | Workbook field | Example | Meaning |
| --- | --- | --- | --- |
| Signal identity | Tag Name / IO Type | 320-FT -20645-A / AIR | An analog input signal from a field transmitter. |
| Cable routing | Field Cable No / Pair | 320-CE-0001 / Pair 1 | The signal uses pair 1 of the identified multicore cable. |
| Termination | CHARM TB Part No | SE4501 | Conductors land on a Standard CHARM Terminal Block. |
| Signal conditioning | CHARM Type | SE4303T01 | AI 4-20 mA HART CHARM is selected for the AIR signal. |
| Physical address | Baseplate / Channel / CHARM | 001-CBP-2 / 1 / 13 | Channel 1 on baseplate 2 of CIOC 001; CHARM position 13. |
| Marshalling hierarchy | CIOC / Cabinet | P30DCIOC3201001 / P30-DCM-32001-01 | The baseplate is installed under this CIOC in this marshalling cabinet. |
| Control ownership | Controller / System Cabinet | P30DPK320101 / P30-DCS-32001-01 | DeltaV software assigns the CIOC/channel to this controller in this system cabinet. |
| Usage classification | Tag Status | Field | The row is an actual plant signal, not spare capacity. |

Do not allocate from only one side A cable-only allocation can create hardware conflicts. A hardware-only allocation can break cable grouping. A controller-only allocation can violate field segregation. Work across the complete row and check the relationships.

# Understanding the naming conventions

The workbook uses compact names that carry location, equipment type and sequence information. The following breakdown explains the project pattern visible in the file. The approved project naming procedure remains the controlling document.

| Item | Example | Project-pattern breakdown |
| --- | --- | --- |
| System cabinet | P30-DCS-32001-01 | P30 = technical room/location prefix; DCS = system cabinet type; 32001 = area/risk-area code used by the project; 01 = cabinet sequence. |
| Marshalling cabinet | P30-DCM-32001-04 | P30 = technical room/location prefix; DCM = DeltaV marshalling cabinet type; 32001 = area/risk-area code; 04 = cabinet sequence. |
| Controller | P30DPK320102 | P30 = location prefix; DPK = project controller identifier; 3201 = compressed area/risk-area segment; 02 = controller sequence. |
| CIOC / CSLS | P30DCIOC3201013 | P30 = location prefix; DCIOC = CIOC identifier; 3201 = compressed area/risk-area segment; 013 = CIOC sequence. |
| Baseplate | 013-CBP-6 | 013 = parent CIOC sequence; CBP = CHARM baseplate; 6 = baseplate number within that CIOC. |
| Marshalling visualization | P30-DCM-32001-04(F) | Cabinet name plus F or R to identify the front or rear cabinet side used for visualization/installation. |

## Baseplates, channels and CHARM numbers

Each CIOC in this exercise uses eight baseplates. Each baseplate has 12 channel positions, giving 96 CHARM positions per CIOC.

CHARM number formula CHARM_No = (baseplate number - 1) x 12 + channel number. Example: baseplate 6, channel 9 gives (6 - 1) x 12 + 9 = 69. This is why 013-CBP-6 / channel 9 appears as CHARM 69.

## Wired-spare tag naming

The spare tag identifies the allocation address so that the installed spare is traceable before it receives a future process tag.

| Example segment | Meaning in 3201DSP0201369 |
| --- | --- |
| 3201 | Area/risk-area segment used by the project. |
| DSP | DeltaV spare-point identifier. |
| 02 | Controller sequence. |
| 013 | CIOC sequence. |
| 6 | Baseplate number. |
| 9 | Channel number. |

Channel numbers may contain one or two digits, so read the tag together with the Controller, CIOC/CSLS, Baseplate and Channel_No columns rather than relying on character count alone.

# Field, Wired Spare and Spare Slot

The Tag Status field distinguishes an operating signal from installed spare capacity and from empty future space.

| FIELD | WIRED SPARE | SPARE SLOT |
| --- | --- | --- |
| Real instrument signal Cable pair, CHARM and terminal block are assigned. The row carries the actual field tag and engineering data. | Installed spare channel Cable pair is wired and the correct CHARM/TB is installed for a defined IO type. A controlled spare tag is used. | Reserved physical position The pair/channel position is reserved, but no functional CHARM is allocated. The sample uses a CHARM protection cover. |

| Status | Tag | IO type | CHARM | Cable pair | Student rule |
| --- | --- | --- | --- | --- | --- |
| Field | Actual process tag | Defined | Correct functional CHARM | Assigned | Complete all engineering fields and confirm the end-to-end path. |
| Wired Spare | Controlled spare tag | Defined | Installed for that IO type | Wired | Count it in the wired-spare allowance and keep its address traceable. |
| Spare Slot | - | - | Protection cover / no functional CHARM | Reserved pair or position | Do not populate a functional CHARM or invent a process tag. |

Workbook illustration The original sample contains 236 allocation rows: 166 Field, 21 Wired Spare and 49 Spare Slot. These counts describe the training sample only; they are not a universal design ratio.

# Selecting the CHARM and terminal block

Start from the real electrical signal, not only the instrument description. Confirm IO Type, signal level, power arrangement, contact type, load current, inrush current, isolation requirement and the approved hardware typical.

| IO Type | Typical duty | CHARM observed in sample | Terminal block observed | Allocation note |
| --- | --- | --- | --- | --- |
| AIR | 4-20 mA/HART analog input | SE4303T01 - AI 4-20 MA HART CHARM | SE4501 - Standard CHARM Terminal Block | Used for transmitters and installed AIR spares. |
| AOR | 4-20 mA/HART analog output | SE4304T01 - AO 4-20 MA HART CHARM | SE4501 - Standard CHARM Terminal Block | Used for control valves, indicators/exchange signals and AOR spares. |
| DIR | 24 VDC dry-contact input | SE4301T02 - low-side-sense discrete input | SE4501 - Standard CHARM Terminal Block | Used for limit switches, hand switches and similar contacts. |
| DOR - high-current load | Solenoid valve; project also requires this check for horn, beacon and sounder duties | SE4302T02 - DO 24 VDC Isolated | SE4502 - Fused-Injected-Power Terminal Block | Check load and inrush; injected power and fuse selection must match the design. |
| DOR - other duty | Alarm/indication and other suitable 24 VDC output duties | SE4302T01 - 24 VDC HIGH SIDE | SE4501 - Standard CHARM Terminal Block | A relay output terminal block may be required where the project needs relay isolation/contact interfacing. |

Critical DO check Do not select a DO CHARM only because the IO Type says DOR. Solenoids, horns, beacons and sounders can draw higher steady-state or inrush current. Verify the load data, power source, fuse, terminal-block arrangement, isolation and project typical before confirming the hardware.

## What Spare Slot means for hardware

A Spare Slot preserves capacity without committing a functional IO type. In the sample, the CHARM Type is SE6103 and the description is CHARM PROTECTION COVER. This is different from a Wired Spare, which already carries the correct functional CHARM and terminal block for its planned IO type.

# Basic allocation rules

## Group logically before filling channels

- Keep signals from the same operating area, equipment package, unit or functional group together where practical.

- Preserve the field-cable sequence so cable pairs can be checked directly against channel assignments.

- Avoid unnecessary mixing of unrelated systems when it makes commissioning, troubleshooting or segregation harder.

- Balance good grouping with controller loading, available CHARM types, baseplate capacity and spare requirements.

## Respect IO segregation

Segregation codes identify the train, duty or separation philosophy that must be preserved. The workbook includes A, B, C, D, E, A-CONTROL and B-ALARM. Project philosophies may also use A-B and B-A for mixed or cross-train relationships.

- Do not place redundant A and B duties together merely to fill a baseplate if the project requires physical or controller separation.

- Keep control and alarm segregation consistent with the approved cause-and-effect, control philosophy and cabinet arrangement.

- Treat A-B, B-A and similar codes as project-defined instructions; confirm their exact meaning instead of assuming.

## Keep cable, IO type and hardware consistent

- A field cable pair must map to one intended signal row unless an approved wiring typical explicitly states otherwise.

- The IO Type, CHARM Type, terminal block and hardware loop typical must describe the same electrical arrangement.

- The Baseplate, Channel_No and CHARM_No must agree mathematically and must belong to the stated CIOC/CSLS.

- The CIOC/CSLS must belong to the stated marshalling cabinet and must be assigned to the stated controller in DeltaV software.

Project-specific cabinet-alarm practice For this project, the first baseplate of each marshalling cabinet was reserved for cabinet alarms. This is a project choice, not a universal DeltaV requirement. Other customers may reserve a different baseplate, use a separate cabinet-alarm philosophy or distribute the alarms differently.

# Spare and future-capacity philosophy

Spare capacity has two different purposes: installed capacity that is immediately usable and empty physical capacity for future expansion. They must be planned and reported separately.

| Capacity type | Project rule for this exercise | How it appears |
| --- | --- | --- |
| Wired spare | 10% by IO Type, calculated per controller | Cable pair wired, spare tag created, IO type defined, correct CHARM/TB installed, Tag Status = Wired Spare. |
| Future spare space | 10% future capacity | Unallocated positions/baseplates kept available; Tag Status = Spare Slot where individual positions are shown. |
| Unconnected baseplates | Typical target: 3-4 baseplates in a 32-baseplate marshalling cabinet | Baseplates are intentionally left free for future cables and future IO; exact quantity is customer specific. |

With four CIOCs, eight baseplates per CIOC and 12 channels per baseplate, one fully equipped marshalling cabinet represents 32 baseplates and 384 channel positions. Capacity planning should still be performed by IO type and controller; the total number of open positions alone does not prove that the correct spare mix exists.

Why 10% must be checked by IO type Ten unused AI positions do not satisfy a DO spare requirement. Calculate AIR, AOR, DIR and DOR spares independently for each controller, apply the project rounding rule, and confirm that the physical CHARM/TB mix matches the count.

The 10% values and the target of 3-4 free baseplates are the philosophy used for this exercise. Customer specifications, contractual spare requirements, cabinet heat/loading limits and future expansion plans can change them.

# A practical allocation workflow

- Prepare and validate the input list. Confirm tag, service, IO type, signal type/level, IS status, equipment, operating area, segregation and cable information.

- Establish controller and cabinet boundaries. Map each operating/risk area and segregation group to the approved system cabinet, controller and marshalling cabinet.

- Plan the marshalling hierarchy. Confirm the CIOC/CSLS list, baseplate ranges, reserved cabinet-alarm baseplate and available expansion baseplates.

- Group cables and signals logically. Keep cable pairs in sequence and preserve train, equipment and functional segregation.

- Select CHARM and terminal block. Use the electrical signal and load requirements, then confirm the approved hardware loop typical.

- Assign baseplate, channel and CHARM number. Use a free position and verify the CHARM number formula.

- Add wired spares. Calculate 10% by IO type per controller and create traceable spare tags with the correct hardware.

- Reserve future space. Keep the required spare slots and unconnected baseplates without installing functional CHARMs unnecessarily.

- Complete DeltaV software assignment. Assign each CIOC/CSLS to the intended controller and align the software channel definition with the allocation.

- Perform independent checks. Reconcile tags, cables, channels, hardware, cabinets, controller ownership, spare counts and segregation before issue.

# Quality checks before issuing the allocation

| Check area | Questions the reviewer should answer |
| --- | --- |
| Completeness | Does every actual field tag have a cable, pair, physical channel, CHARM/TB, CIOC, cabinet and controller? |
| Uniqueness | Is any cable pair, channel or CHARM number duplicated within the same physical hierarchy? |
| Address logic | Does CHARM_No agree with baseplate and channel? Does the baseplate prefix agree with the CIOC sequence? |
| Hardware match | Do IO Type, signal level, CHARM, terminal block, external power and loop typical agree? |
| DO loading | Were solenoid/horn/beacon/sounder current, inrush, fuse and injected-power requirements checked? |
| Segregation | Are A/B and other train or functional separations preserved across cables, baseplates, CIOCs and controllers? |
| Spare compliance | Is 10% wired spare provided by IO type per controller, and is future space separately available? |
| Cabinet capacity | Are sufficient baseplates and channels available after field signals, cabinet alarms and wired spares? |
| Status discipline | Are actual signals marked Field, installed spares marked Wired Spare, and unpopulated positions marked Spare Slot? |
| Software alignment | Does the DeltaV controller/CIOC/channel configuration match the issued allocation? |
| Change traceability | Are revision number, remarks, old tag and change type updated where relocation, deletion or renaming occurred? |

## Common mistakes to avoid

- Using Spare Slot for a position where a CHARM has actually been installed.

- Calling a spare Wired Spare without defining an IO type or installing the correct CHARM/TB.

- Selecting Standard TB for a higher-current DO without checking injected power and fuse requirements.

- Mixing A and B trains because adjacent channels are available.

- Providing 10% total spare channels but not 10% for each IO type per controller.

- Leaving DeltaV controller assignment inconsistent with the cabinet and CIOC naming.

- Copying a project-specific naming or cabinet-alarm rule into another project without confirmation.

# Scope boundary: IRC and MCC signals

This training guide intentionally does not develop the detailed allocation method for IRC signals or MCC signals. Their cabling is internal to the solution, is decided by Emerson and requires additional design criteria, interfaces and project-specific rules.

Future expansion topic Treat IRC/MCC allocation as a separate advanced module. Do not force those signals into the simplified field-cable-to-CHARM method in this guide without the applicable architecture, internal cabling, relay/interface and customer requirements.

## What students should remember

- IO Allocation connects field wiring, cabinet hardware and DeltaV software in one controlled record.

- The cable pair and the CHARM channel are two ends of the same traceable path.

- Controller ownership is a software assignment, but it must match the physical cabinet hierarchy.

- Naming conventions encode location and sequence; decode them before allocating.

- Field, Wired Spare and Spare Slot are different engineering states and must not be interchanged.

- CHARM and terminal-block selection follows the electrical signal and load, not only the tag description.

- Logical grouping, segregation and spare philosophy must be applied per the approved project rules.

- A clean allocation is one that another engineer can wire, configure, test and troubleshoot without assumptions.

# Quick-reference sheet

| Item | Rule / example |
| --- | --- |
| Physical path | Field device -> field cable -> cable pair -> CHARM TB -> CHARM -> baseplate/channel -> CIOC/CSLS. |
| Software path | CIOC/CSLS and channel -> assigned in DeltaV software -> controller -> system cabinet. |
| CIOC capacity | 8 baseplates x 12 channels = 96 positions. |
| Marshalling cabinet example | 4 CIOCs x 8 baseplates = 32 baseplates; 384 total positions. |
| CHARM number | (Baseplate - 1) x 12 + Channel. |
| Wired spare | Correct IO-specific CHARM/TB installed and cable pair wired; controlled spare tag used. |
| Spare slot | No functional CHARM; position protected/reserved for the future. |
| Spare allowance | 10% by IO type per controller, plus 10% future space for this exercise. |
| Higher-current DOR | Check isolated DO, fused injected power, load/inrush, fuse and external power. |
| Customer-specific items | Cabinet-alarm baseplate, spare percentages, unconnected baseplates, segregation codes and naming details. |

Document basis and limitation: Workbook examples and counts come from Sample_IO_Allocation_VIT.xlsx. Design philosophies such as 10% spares, first-baseplate cabinet alarms and 3-4 unconnected baseplates are the project rules supplied for this VIT exercise. Apply the customer-approved project documents on live work.